STANDARD FEATURES:

(	Long – life energy efficient L.E.D. Lamps

- Rugged 20 gauge All Steel frame

- White baked on finish

- Universal input for 120 and 277 Volt AC

- Built–in down light provides light output at floor level below

BATTERY BACKUP PACK FEATURES:

- Solid State charging current limited

- Solid State overload and short circuit protection

- Brownout protection

- Solid State line latched, Low voltage disconnect to protect battery against deep discharge

- Reverse Battery Polarity Protection

- MEETS OR EXCEEDS UL, NEC, OSHA, NPFA Life Safety Code and other state and local codes

DESCRIPTION:

The ADA-IS or ADA-IS-UL are designed to provide a maintenance-free, highly visible

AREA OF RESCUE ASSISTANCE legend

Under all lighting conditions. These signs use high brilliance, high reliability L.E.D.’S as their internal light source. Power consumption is less than 5 watts for most of these units and anticipated lamp life is more than 50 years.

The ADA-IS is available with red L.E.D.’s and double face configurations, included is the low profile canopy for ceiling or end mount. The ADA-IS-UL is supplied standard with long life sealed Nickel Cadmium Battery.

The ADA-IS and ADA-IS-UL units use the latest design in accomplishing its task by using indirect LED’s to light the illuminated sign “cavity” while meeting all codes regarding illumination.

# (ADA-IS or ADA-IS-UL)

# (8.25”L x 12.25”W x 2.25”D)

# TEST OPERATION:

# To test, depress the stencil marked “PRESS HERE TO TEST”.  The “Charge Indicator” LED will Blink and the DC mode will come on.

# Release the test switch. DC mode will quit and the charge indicator LED will come on signifying AC operation.

# Bright Charge LED indicates a high charge rate after battery is fully charged, the indicator LED will be dim.

# MAINTENANCE:

# Code requires that the equipment be tested every 30 days for 30 seconds and that written records be maintained. Further, the equipment is to be tested once a year for 90 minutes .The battery is to be replaced or the equipment repaired, whenever the equipment fails to operate as intended during the 90 minute test.

# Text boxes

| AREA OF |  |
| --- | --- |
| RESCUE |  |

ASSISTANCE